Post Safety Dossier

SAFETY HYGIENE ERGONOMICS

PROCESS: US2 Group 11 & 12 Alert Matrix

There is a known issue with the Group 11 & 12 fire suppression system infrastructure related to the pipe schedule installed during original construction. The long-term corrective action is to replace the existing piping with Schedule 80 piping. This upgrade will be completed in phases; therefore, intermittent leaks are expected until the replacement is complete. This alert matrix defines how to respond to leaks quickly and consistently, including who to contact, when to notify stakeholders, and how to document the event.

If a leak occurs on Group 11 or 12, follow the decision flow below to reduce safety and quality risk and to minimize impact to plant performance.

- When a leak is reported, the MP2 on the group will identify the source and contact the Security team.

- Security will assess the leak for potential safety risks to personnel in the area and/or quality risks to the process.

  - Security will communicate the event via standard email distribution, including that a fire-suppression leak occurred and who was notified.

- If a safety risk is identified:

  - MP2 or the Machine Spoke will create a work order (WO) and notify the NZB TS team.

  - The NZB TS team will assess whether the leak can be contained.

  - If containable:

    - Implement containment (e.g., pipe patch or tarps with catch bins), as appropriate.

    - Close the WO with comments describing the containment method and the leak location.

    - Email the Production BUL and Christian with the patch type and location to maintain traceability of leaks and repairs.

  - If not containable:

    - Notify Security that the leak is not containable.

    - Security will notify Christian.

      - Notify Pye-Barker and request emergency response.

      - Christian will determine whether the leak can be isolated to minimize risk to operations in unprotected areas.

        - Initiate required communications and the approval process.

      - Christian and MP2 will define a plan and timeline to (1) repair the leak and (2) complete any required work in the area using additional safety controls.

      - Share the plan with the Group 11/12 BUL, Group 11/12 MR, Group 11/12 RSTec, RTA, and the ZB Shop Manager.

- If a quality risk is identified:

  - MP2 will contact C3P and create a WO to notify the NZB TS team.

  - C3P and the NZB TS team will assess whether the leak can be contained.

  - If containable:

    - Implement containment (e.g., pipe patch or tarps with catch bins), as appropriate.

    - C3P and MP2 will confirm whether containment is sufficient to maintain operation and quality performance.

    - Close the WO with comments describing the containment method and the leak location.

    - Email the Production BUL, Christian Alfaro, and Michael Hurst with the patch type and location to maintain traceability of leaks and repairs.

  - If not containable:

    - Notify Security that the leak is not containable.

    - Security will notify Christian.

      - Notify Pye-Barker and request emergency response.

      - Christian will determine whether the leak can be isolated to minimize risk to operations in unprotected areas.

        - Initiate required communications and the approval process.

      - Christian and MP2 will define a plan and timeline to (1) repair the leak and (2) complete any required work in the area using additional safety controls.

      - Share the plan with the Group 11/12 BUL, Group 11/12 MR, C3P Team, Group 11/12 RSTec, Michael Hurst, RTA, and the ZB Shop Manager.